{"text_format":"2","workbook":"xlsx","n_sheets":13,"sheets":["Standard","Special","9400","NG-900","AR4100","AR5100","Candy Cane","B-19434B","C-19434B","NR","NRF-9430","UA3149A","PRV"],"not_rendered":{"charts":0,"images":33,"macros":0,"external_links":0,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"Standard","index":0,"n_rows":48,"n_cols":11,"rows_kept":48,"cut":false,"hidden":false,"merged":[[12,0,12,10],[13,1,14,1],[8,8,10,8],[8,9,10,9],[17,4,19,4],[17,6,19,6],[17,7,19,7],[17,8,19,8],[17,9,19,9],[0,0,0,10],[7,0,7,10],[8,1,10,1],[8,4,10,4],[8,6,10,6],[8,7,10,7],[8,10,10,10],[3,1,3,6],[44,1,47,1],[38,10,41,10],[43,0,43,10],[44,10,47,10],[38,6,41,6],[38,7,41,7],[38,8,41,8],[38,9,41,9],[44,6,47,6],[44,7,47,7],[44,8,47,8],[44,9,47,9],[38,1,41,1],[31,0,31,10],[32,6,35,6],[32,7,35,7],[37,0,37,10],[32,8,35,8],[32,9,35,9],[32,1,33,1],[28,1,29,1],[26,1,27,1],[22,1,23,1],[22,4,23,9],[13,4,14,9],[25,0,25,10],[16,0,16,10],[17,1,19,1],[17,10,19,10],[21,0,21,10],[26,4,29,4],[26,5,29,9],[26,10,29,10],[26,2,27,2],[28,2,29,2],[27,3,29,3]]}
["Overview RegO Relief Valves"]
["Version","28-1-2021"]
[{"$nulls":9},"PSI","Bar"]
["Notes","Nearly all Relief Valves from this page can be set in our own EU factory, within 2 weeks delivery time\nNearly all Settings can be made within the range as mentioned below in:  Pressure Range Setting",{"$nulls":6},"Calculator from PSI to Bar",500,{"$f":"J4/14.5038","v":34.473724127470042}]
[]
["Style","Product Pictures","Inlet Size","Outlet Size","Pressure Range Setting","Set At","Gas","Liquid","Flow Capacity/Kv Factor","Certification","Remarks"]
[]
["Relief Valve, Non-ASME 9400 Series- Brass Body and Valve Material"]
["PRV9432","Click picture for detailed info","1/4\"  M.NPT","3/4-20 UNF-2B THD","0.68 - 41.36 Bar","RegO GmbH","   Oxygen\n   Nitrogen\n   Argon\n   Helium\n   Hydrogen\n   CO2\n   Natural Gas\n   Air\n   N2O","Use Candy Cane !\nOxygen\nNitrogen\nArgon\nCO2\nLNG\nN2O","See the Flow Capacity in the \ndetailed excell page below\n\n","PED\nTPED\nE4-110R (automotive)"," F  for Fluorosilicone for Pressure Range: 1.10 - 9.58 Bar\n\n T  for PTFE for Pressure Range: 9.65 - 41.36 Bar\n\n N  for B-9425 and B-9426, Fluorosilicone seat, all set pressures\n\n*Insert  P  if you want no drain hole, in case of Pipe Away Option\n Set Point Tolerance +- 3%\nExample Part Number:  PRV9432TP: 18.2B"]
["PRV9433",null,"3/8\"  M.NPT","3/4-20 UNF-2B THD",null,"RegO GmbH"]
["PRV9434",null,"1/2\"  M.NPT","3/4-20 UNF-2B THD",null,"RegO GmbH"]
[]
["Optional:  Pipe Away Connector, to connect a blow off pipe to the outlet of the PRV"]
["B-9412-2","Click picture for detailed info","3/4-20 UNF-2B THD","3/8\"  F.NPT"]
["B-9412-4",null,"3/4-20 UNF-2B THD","1/2\"  F.NPT"]
[]
["Relief Valve, Non-ASME 9400 Series- Stainless Steel Body and Valve Material"]
["SS9432","Click picture for detailed info","1/4\"  M.NPT","3/4-20 UNF-2B THD","0.68 - 41.36 Bar","RegO GmbH","   Oxygen\n   Nitrogen\n   Argon\n   Helium\n   Hydrogen\n   CO2\n   Natural Gas\n   Air\n   N2O","Use Candy Cane !\nOxygen\nNitrogen\nArgon\nCO2\nLNG\nN2O","See the Flow Capacity in the \ndetailed excell page below\n\n","PED\nTPED"," F  for Fluorosilicone for Pressure Range: 1.10 - 9.58 Bar\n\n T  for PTFE for Pressure Range: 9.65 - 41.36 Bar\n\n N  for B-9425 and B-9426, Fluorosilicone seat, all set pressures\n\n*Insert  P  if you want no drain hole, in case of Pipe Away Option\n Set Point Tolerance +- 3%\nExample Part Number:  SS9432TP: 18.2B"]
["SS9433",null,"3/8\"  M.NPT","3/4-20 UNF-2B THD",null,"RegO GmbH"]
["SS9434",null,"1/2\"  M.NPT","3/4-20 UNF-2B THD",null,"RegO GmbH"]
[]
["Optional:  Pipe Away Connector, to connect a blow off pipe to the outlet of the PRV"]
["SS-9412-2\nNot available yet","Click picture for detailed info","3/4-20 UNF-2B THD","3/8\"  F.NPT",{"$nulls":6},"Carlos created a CO 29-4-2020"]
["SS9412-4",null,"3/4-20 UNF-2B THD","1/2\"  F.NPT"]
[]
["Candy Cane Riser Tubes"]
["1332SS","Click picture for detailed info","Tubing\n0.375\"","1/4\" FNPT","41.37 Barg",{"$nulls":5},"Tubing…............Stainless Steel\nFitting…........................Brass"]
["1334SS",null,null,"1/2\" FNPT"]
["1344SS","Click picture for detailed info","1/2\" MNPT"]
["1344SSA"]
[]
["Right Angle Relief Valve NG-900 Series- Brass Body and Valve Material"]
["NG9002T","Click picture for detailed info","1/4\"  M.NPT","3/8\"  F.NPT","1-31.6 Bar","RegO GmbH","   Oxygen\n   Nitrogen\n   Argon\n   Helium\n   Hydrogen\n   CO2\n   Natural Gas\n   Air\n   N2O","   Oxygen\n   Nitrogen\n   Argon\n   Helium\n   Hydrogen\n   CO2\n   Natural Gas\n   Air\n   N2O",null,"PED\nTPED\nE4-110R (NG9002 & NG9008)"]
["NG9003T",null,"3/8\"  M.NPT","3/8\"  F.NPT","\nSettings available:\n15.8 Bar\n17.2 Bar\n19.0 Bar\n24.1 Bar\n28.6 Bar\n\n","RegO GmbH",{"$nulls":4},"New Pressure Settings on request."]
["NG9004T\nNot available yet",null,"1/2\"  M.NPT\nNot available yet","3/8\"  F.NPT\nNot available yet","1-31.6 Bar\nNot available yet","RegO GmbH",{"$nulls":4},"Carlos has created a CO Request in order \nto create this new part (22-4-2020)"]
["NG9008M","Click picture for detailed info","SAE J514\n","3/8\"  F.NPT","Fixed Settings\n\n230 PSI\n250 PSI\n320 PSI","ECI"]
[]
["Angle Relief Valve, AR4100 Series - NPT connections"]
["AR4104","Click picture for detailed info","1/2\"  M.NPT","1\"  F.NPT","5.17 - 39.03 Bar","RegO GmbH","   Oxygen\n   Nitrogen\n   Argon\n   Helium\n   Hydrogen\n   CO2\n   Natural Gas\n   Air\n   N2O","   Oxygen\n   Nitrogen\n   Argon\n   Helium\n   Hydrogen\n   CO2\n   Natural Gas\n   Air\n   N2O","See the Flow Capacity in the \ndetailed excell page below\n\n","PED\nTPED\nASME  (when set at USA)\nCRN    (when set at USA)"]
["AR4106",null,"3/4\"  M.NPT","1\"  F.NPT","5.17 - 39.03 Bar","RegO GmbH"]
["AR4108",null,"1\"  M.NPT","1-1/4\"  F.NPT","2 - 27.58 Bar","RegO GmbH"]
["AR4112B",null,"1-1/2\"  M.NPT","2\"  F.NPT","2.75 - 29.90 Bar","RegO GmbH"]
[]
["Angle Relief Valve, AR5100 Series - BSP connections"]
["AR5104","Click picture for detailed info","1/2\"  M.BSPT","1\"  F.BSPT","5.17 - 39.03 Bar","RegO GmbH","   Oxygen\n   Nitrogen\n   Argon\n   Helium\n   Hydrogen\n   CO2\n   Natural Gas\n   Air\n   N2O","   Oxygen\n   Nitrogen\n   Argon\n   Helium\n   Hydrogen\n   CO2\n   Natural Gas\n   Air\n   N2O","See the Flow Capacity in the \ndetailed excell page below\n\n","PED\nTPED\nASME  (when set at USA)\nCRN    (when set at USA)"]
["AR5106",null,"3/4\"  M.BSPT","1\"  F.BSPT","5.17 - 39.03 Bar","RegO GmbH"]
["AR5108",null,"1\"  M.BSPT","1-1/4\"  F.BSPT","2 - 27.58 Bar","RegO GmbH"]
["AR5112B",null,"1-1/2\"  M.BSPT","2\"  F.BSPT","2.75 - 29.90 Bar","RegO GmbH"]

{"sheet":"Special","index":1,"n_rows":40,"n_cols":11,"rows_kept":40,"cut":false,"hidden":false,"merged":[[9,0,9,10],[14,0,14,10],[10,10,12,10],[15,4,17,4],[15,6,17,6],[15,7,17,7],[10,7,12,7],[10,8,12,8],[15,10,17,10],[10,1,12,1],[15,1,17,1],[10,4,12,4],[10,6,12,6],[23,1,24,1],[15,8,17,8],[19,0,19,10],[22,0,22,10],[23,4,24,4],[23,6,24,6],[23,7,24,7],[23,8,24,8],[0,0,0,10],[5,0,5,10],[6,1,7,1],[6,7,7,7],[6,8,7,8],[3,1,3,6],[36,8,39,8],[26,0,26,10],[29,0,29,10],[32,0,32,10],[35,0,35,10],[36,4,39,4],[36,5,39,5],[36,6,39,6],[36,1,39,1],[36,7,39,7]]}
["Overview RegO Relief Valves"]
["Style","Product Pictures","Inlet Size","Outlet Size","Pressure Range Setting","Set At","Temperature Range","Gas","Liquid","Certificate","Remarks"]
[]
["Notes","All Relief Valves from this page are Special and are being set in USA manufacturing, lead time is 60-90 days\nAll settings can be made within the range as mentioned below in in Pressure Range Setting"]
[]
["Relief Valve, Non-ASME 9400 Series- Brass Body and Valve Material"]
["B-9425",null,"3/4\" M.NPT","1\" F.NPT","1.37 - 20.68 Bar","ECI","Flurosilicone Seat (-51°C to +74°C)","Oxygen\nNitrogen\nArgon\nHelium\nHydrogen\nCO2\nNatural Gas\nAir\nN2O","Use Candy Cane !\nOxygen\nNitrogen\nArgon\nCO2\nLNG\nN2O",null," N for B-9425 and B-9426, Fluorosilicone seat, all set pressures\n Set Point Tolerance +/- 3%\n Insert P if no drain hole"]
["B-9426",null,"1\" M.NPT","1-1/4\" F.NPT","4.13-20.68 Bar","ECI","Flurosilicone Seat (-51°C to +74°C)",null,null,null,"  N for B-9425 and B-9426, Fluorosilicone seat, all set pressures\n  Set Point Tolerance +/- 3%\n  Insert P if no drain hole"]
[]
["Relief Valve, ASME PRV19430 Series- Brass Body and Valve Material"]
["PRV19432",null,"1/4\" M.NPT",null,"1.17  -  41.36 Bar","ECI","Teflon Seat (-196°C to +74°C)\nFluorosilicone Seat (-51°C to +74°C)","Oxygen\nNitrogen\nArgon\nHelium\nHydrogen\nCO2\nNatural Gas\nAir\nN2O","Use Candy Cane !\nOxygen\nNitrogen\nArgon\nCO2\nLNG\nN2O",null,"  F for Fluorosilicone for PRV and SS Styles 6.2 - 9.5 Bar\n  T for PTFE for PRV and SS Styles 9.6 - 41.4 Bar\n  Set Point Tolerance +/- 3%\n  Insert P if no drain hole"]
["PRV19433",null,"3/8\" M.NPT",null,null,"ECI"]
["PRV19434",null,"1/2\" M.NPT",null,null,"ECI"]
[]
["Relief Valve, ASME PRV29430 Series- Stainless Steel  Body and Valve Material"]
["PRV29432",null,"1/4\" M.NPT",null,"1.17  -  41.36 Bar","ECI","Telfon Seat (-196°C to +74°C)\nFluorosilicone Seat (-51°C to +74°C)","Oxygen\nNitrogen\nArgon\nHelium\nHydrogen\nCO2\nNatural Gas\nAir\nN2O","Use Candy Cane !\nOxygen\nNitrogen\nArgon\nCO2\nLNG\nN2O",null,"  F for Fluorosilicone for PRV and SS Styles 6.2 - 9.5 Bar\n  T for PTFE for PRV and SS Styles 9.6 - 41.4 Bar\n  Set Point Tolerance +/- 3%\n  Insert P if no drain hole"]
["PRV29433",null,"3/8\" M.NPT",null,null,"ECI"]
["PRV29434",null,"1/2\" M.NPT",null,null,"ECI"]
[]
["Noise Reduction Relief Valve NRF9430 Series- Brass Body and Valve Material"]
["NRF9432T",null,"1/4\" M.NPT",null,"1.17  -  41.36 Bar","ECI","-196°C to +74°C","Oxygen\nNitrogen\nArgon\nHelium\nHydrogen\nCO2\nNatural Gas\nAir\nN2O","Use Candy Cane !\nOxygen\nNitrogen\nArgon\nCO2\nLNG\nN2O",null,"  Substantial reduction of discharge noise"]
[]
["Noise Reduction Relief Valve NR Series- Brass Body and Valve Material"]
["NR9432F",null,"1/4\" M.NPT",null,"1.17  -  41.36 Bar","ECI","-196°C to +74°C","Oxygen\nNitrogen\nArgon\nHelium\nHydrogen\nCO2\nNatural Gas\nAir\nN2O","Use Candy Cane !\nOxygen\nNitrogen\nArgon\nCO2\nLNG\nN2O",null,"  50% reductoin in outlet noise related to standard relief valve.\n  Seat Material Fluorosilicone"]
["NR9432T",null,"1/4\" M.NPT",null,null,"ECI",{"$nulls":4},"  50% reductopn in outlet noise related to standard relief valve.\n  Seat Material PTFE"]
[]
["Cryogenic Gas Relief Valves, ASME B-19434B Series"]
["B-19434B",null,"1/2\" M.NPT","1/2\" F.NPT","235 to 375 PSI","ECI","-51°C to +74°C","Oxygen\nNitrogen\nArgon\nHelium\nHydrogen\nNatural Gas\nAir\n","None","ASME rated. certified","  When the pressure increases beyond a predetermined point, \n  the valve opens to its full discharge Capacity in order \n  to quickly reduce excess pressure."]
[]
["Cryogenic Gas Relief Valve, ASME C-19434B Series"]
["C-19434B",null,"1/2\" M.NPT","1\" F.NPT","250 to 375 PSI","ECI","-40°C to +74°C","CO2\nN2O","LCO2","ASME rated. certified","Designed for use with Carbon Di Oxide\nSeat disc:  EPDM Synthetic Rubber"]
[]
["Carbon Dioxide Relief Valve, ASME UA3149A Series"]
["UA3149A",null,"2-1/2\" M.NPT","3\" F.NPT","20 Bar to 24.7 Bar","ECI","-40°C to +29°C","CO2","LCO2"]
[]
["PRV Series (Air Service)"]
["PRV250BR",null,"1/4\" M.NPT",null,"17-600 PSI","ECI","-196°C to +74°C","Air","None"]
["PRV250B",null,"1/4\" M.NPT"]
["PRV500BR",null,"1/2\" M.NPT"]
["PRV500B",null,"1/2\" M.NPT"]

{"sheet":"9400","index":2,"n_rows":0,"n_cols":0,"rows_kept":0,"cut":false,"hidden":false,"merged":[]}

{"sheet":"NG-900","index":3,"n_rows":0,"n_cols":0,"rows_kept":0,"cut":false,"hidden":false,"merged":[]}

{"sheet":"AR4100","index":4,"n_rows":0,"n_cols":0,"rows_kept":0,"cut":false,"hidden":false,"merged":[]}

{"sheet":"AR5100","index":5,"n_rows":0,"n_cols":0,"rows_kept":0,"cut":false,"hidden":false,"merged":[]}

{"sheet":"Candy Cane","index":6,"n_rows":0,"n_cols":0,"rows_kept":0,"cut":false,"hidden":false,"merged":[]}

{"sheet":"B-19434B","index":7,"n_rows":0,"n_cols":0,"rows_kept":0,"cut":false,"hidden":false,"merged":[]}

{"sheet":"C-19434B","index":8,"n_rows":0,"n_cols":0,"rows_kept":0,"cut":false,"hidden":false,"merged":[]}

{"sheet":"NR","index":9,"n_rows":0,"n_cols":0,"rows_kept":0,"cut":false,"hidden":false,"merged":[]}

{"sheet":"NRF-9430","index":10,"n_rows":0,"n_cols":0,"rows_kept":0,"cut":false,"hidden":false,"merged":[]}

{"sheet":"UA3149A","index":11,"n_rows":0,"n_cols":0,"rows_kept":0,"cut":false,"hidden":false,"merged":[]}

{"sheet":"PRV","index":12,"n_rows":0,"n_cols":0,"rows_kept":0,"cut":false,"hidden":false,"merged":[]}